## Slide 1: CyberSkills2Work The National Cybersecurity Workforce Development Program

## Slide 2: Industrial Control Systems Security
This program is funded by the National Security Agency National Centers of Academic Excellence in Cybersecurity (NCAE-C) Program.
For additional information, please visit www.CyberSkills2Work.org.
Acknowledgement
Course Title
CRN
©2024 CyberSkills2Work - Institution Name

## Slide 3: Module 03 – ICS Protocols
Modbus protocol
DNP3 protocol
Serial/Fieldbus-based protocols
Building Automation Systems and BACnet
Other ICS Protocols
Protocols by Purdue Model Layer
Packet analysis of Modbus and DNP3
Security Considerations for ICS Protocols
Overview
Course Title
CRN
©2021 CyberSkills2Work - Institution Name

## Slide 4: Module 03 – ICS Protocols
Baude Rate. Ex: 1200
Bits Per Second (BPS).
BPS = Baud * number of bits per baud
Example: 1200 baud * 8 bits per second = 9600 bps
RS-232, RS-422, RS-485
RS-232 uses -12V/+12V and is made up of 9 wires (some as much as 25)
RS-485 uses -5V/+5V and is made up of 3 wires (DataA, DataB, GND)
Overview
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Baud Rate measures the number of signal intervals or pulses that are transmitted per second.
BPS is a measure of how many bits can be transferred each second. BPS is also measured by how many bits can be sent during one pulse. The technique of sending large bps over a smaller bad rate is called packing. The general technique for "packing" bits into a baud is called quadrature amplitude modulation.
RS-232, 422, and 485 are serial ports or COM ports (meaning Computer Ports). RS-232 is a simple point-to-point standard, while 485 can support multiple distances in a network. 232 is still in use today, but 485 is heavily favored. Just so you know, Ethernet, Firewire, and USB are also serial ports. Other examples are SPI, I2C, and
The example above is the number of bits per second that RS-232, RS-422, and RS-485 can send; however, RS-422 and RS-485 can send said transmissions much farther than RS-232.
Modbus RTU uses all three serial standards.

## Slide 5: Module 03 – ICS Protocols
Modbus RTU
Serial protocol (RS-232/RS-485)
Binary encoding, master-slave communication. *
Modbus ASCII
Serial protocol
ASCII-encoded data, more readable than RTU but slower.
Plain-text
Modbus TCP (modbus over tcp/ip)
Encapsulates Modbus in TCP/IP for Ethernet networks.
Widely used for integrating legacy devices into modern systems.
.
Modbus (including variants)
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: The Modbus protocol family is one of the most widely adopted sets of communication protocols in industrial environments due to its simplicity, open standard status, and compatibility across multiple vendors. Originally designed by Modicon (now Schneider Electric), Modbus follows a master-slave model, where one master issues commands and multiple slave devices respond.
Modbus RTU is the most common and efficient format used over RS-232 or RS-485 serial connections. It transmits data in a compact binary format and includes a CRC for error checking.
Modbus ASCII is less bandwidth-efficient but easier to troubleshoot, as it encodes messages in readable ASCII characters.
Modbus TCP encapsulates Modbus messages within TCP/IP packets and is used over Ethernet networks. It does not use a checksum at the Modbus level because TCP/IP already ensures packet integrity.
This protocol suite is simple but insecure—it lacks encryption or authentication, making it susceptible to spoofing, tampering, and unauthorized writes unless isolated or protected via firewalls and secure gateways. We will cover a Man-In-The-Middle attack on Wednesday.

## Slide 6: Module 03 – ICS Protocols
Modbus Plus (modbus+)
Proprietary high-speed peer-to-peer token-passing network by Modicon (now Schneider Electric).
Uses its own media and protocol.
Not actually a variant of Modbus
Allows omnidirectional communication – does NOT use Master/Slave.
.
Modbus … continued
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: MODBUS PLUS:
Requires a dedicated co-processor to handle fast HDLC-like token rotation. It uses twisted pair at 1 Mbit/s and includes transformer isolation at each node, which makes it transition/edge-triggered instead of voltage/level-triggered. Special hardware is required to connect Modbus Plus to a computer, typically a card made for the ISA, PCI or PCMCIA bus.
Unlike the original Modbus protocol which operates on a master-slave principle, Modbus Plus allows all devices on a network to communicate with each other directly, thereby increasing efficiency and reducing response times.
Modbus Plus uses PCI and PCI-Express adapters. Modbus Plus, often abbreviated as MB+, is a peer-to-peer protocol that allows for fast communication between automation devices. Unlike the original Modbus protocol which operates on a master-slave principle, Modbus Plus allows all devices on a network to communicate with each other directly, thereby increasing efficiency and reducing response times. - RACO

## Slide 7: Module 03 – ICS Protocols
Modbus RTU Packets
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Field | Description
Device Address | 1 byte (0–247)
Function Code | 1 byte
Data | N bytes (depends on function)
CRC | 2 bytes (error checking)
Notes: Instructor Notes:
A typical Modbus RTU frame contains a device address, function code, a variable-length data field, and a Cyclic Redundancy Check (CRC) for error checking. Common function codes include 0x03 (Read Holding Registers) and 0x06 (Write Single Register). The protocol is efficient and used widely in RS-485 bus networks.
RTU Mode When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each eight-bit byte in a message contains two four-bit hexadecimal characters. The main advantage of this mode is that its greater character density allows better data throughput than ASCII for the same baud rate. Each message must be transmitted in a continuous stream.
Coding System Eight-bit binary, hexadecimal 0 ... 9, A ... F Two hexadecimal characters contained in each eight-bit field of the message Bits per Byte 1 start bit 8 data bits, least significant bit sent first 1 bit for even / odd parity-no bit for no parity 1 stop bit if parity is used-2 bits if no parity Error Check Field Cyclical Redundancy Check (CRC)

## Slide 8: Module 03 – ICS Protocols
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
At the beginning of the received PDU (protocol data unit) message, a new 7-byte header is added, which is called MBAP Header (Modbus Application Header). This header has the following data:
Transaction Identifier: 2 bytes are set by the Master to uniquely identify each request. Can be any. These bytes are repeated by the Slave device in the response, since the responses of the Slave device may not always be received in the same order as the requests.
Protocol Identifier: 2 bytes are set by the Master, will always be 00 00, which corresponds to the Modbus protocol.
Length: 2 bytes are set by the Master, identifying the number of bytes in the message that follow. It is counted from Unit Identifier to the end of the message.
Unit Identifier: 1 byte is set to Master. It is repeated by the Slave device to uniquely identify the Slave device.
Refer to the intro_modbus file for more information about Modbus over TCP

## Slide 9: Module 03 – ICS Protocols
Designed for reliable telemetry in electrical substations
Supports:
Time-stamped events
Unsolicited messaging
File transfer
Operates over serial (RS-232/RS-485) and TCP/IP
Defined in IEEE 1815
Open standard protocol, so no fees attached (except a small documentation fee).
.
DNP3 (Distributed Network Protocol)
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
DNP3 addresses many limitations of Modbus, especially in environments where bandwidth and latency are concerns. It supports unsolicited reporting — field devices can send updates without being polled — and includes timestamps for each data point, improving historical accuracy. Widely used in power generation, distribution, and water management. DNP3 uses the term outstation to denote remote computers as are found in the field. The term master is used for the computers in the control centers.
The DNP3 protocol framework includes a library of objects that are usually used in SCADA systems. These objects include:
Binary Inputs
They are used to report gear characteristics that have two different states. For example, power on or off or an access panel is open or closed.
Analog Inputs
This is another common object used to report characteristics that have a range of values. For example, exhaust fan speed can be anywhere from 40 to 400 RPM, or the main power can vary from 110 to 128 VAC.
Purpose and Function:
SCADA Communication:
DNP3 is designed for communication between SCADA components like master stations, RTUs, and other Intelligent Electronic Devices (IEDs).
Data Acquisition and Control:
It enables the collection of data from remote devices and the control of those devices from a central location.
Object-Based Application Layer:
The application layer in DNP3 uses a hierarchical object model, which simplifies the handling of different data types and reduces bit mapping requirements.
Data Link Layer Features:
The data link layer provides features like polling, time synchronization, and error detection and recovery.
Multiple Masters and Peer-to-Peer Operations:
DNP3 supports multiple masters and can also allow for peer-to-peer communication.
2. Key Features:
Object Model:
DNP3 uses objects to represent data, making it easier to handle different data types and structures.
Data Segmentation:
DNP3 can segment messages into smaller frames to improve error handling and recovery.
Efficient Data Transfer:
DNP3 can request and respond with multiple data types in single messages and include only changed data in response messages, optimizing data transfer.
Priority-Based Data Handling:
DNP3 allows for assigning priorities to data items and requesting them periodically based on priority.
Time Synchronization:
DNP3 supports time synchronization and a standard time format.
Unsolicited Reporting:
DNP3 can send data to the master station even without a request, allowing for real-time monitoring of critical events.
Security:
DNP3 can utilize TLS encryption and authentication mechanisms for secure communication, especially important in critical infrastructure systems.
3. Typical Use Cases:
Electric Utilities:
Used for monitoring and controlling power grids, substations, and other electrical infrastructure.
Water Utilities:
Used for monitoring water distribution systems, pumping stations, and other water infrastructure.
Oil and Gas:
Used for monitoring and controlling pipelines, storage facilities, and other oil and gas infrastructure.
Industrial Automation:
Used for various industrial automation tasks, including manufacturing and process control.
4. Benefits of using DNP3:
Reliable Communication:
DNP3 is designed to be robust and reliable, ensuring that data is transmitted accurately even in challenging environments.
Security:
DNP3 can be configured with security features like TLS encryption to protect data from unauthorized access.
Data Integrity:
DNP3 ensures data integrity through error detection and correction mechanisms.
Efficiency:
DNP3 is designed to be efficient, minimizing data transfer overhead and improving communication speed

## Slide 10: Module 03 – ICS Protocols
DNP3 (simplified) packet structure
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Field | Description
Link Layer Header | Start, Length, Control, Destination, Source
Transport Layer | Sequence byte
Application Layer | Function Code, Objects, Qualifiers
CRC | Multiple 2-byte CRCs after each 16 bytes
Notes: Instructor Notes:
DNP3 is layered — each layer (link, transport, application) adds reliability. The Link Layer handles routing and basic control. The Transport Layer ensures packet reassembly, and the Application Layer carries command/data objects with qualifiers. DNP3 uses multiple CRC blocks to ensure error detection across large payloads. The protocol’s robustness makes it well-suited for noisy environments and critical infrastructure.

## Slide 11: Module 03 – ICS Protocols
DNP3 (advanced) packet structure
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
The application layer combines an application service data unit (ASDU), a packaged object in itself, with an application protocol control info (APCI) block to make an application protocol data unit (APDU).
The transport layer breaks the APDU into segments with a maximum size of 16 bytes and packages them with an 8-bit transport control header and 16-bit segment CRC separators into a transportFrame.
The link layer can be mapped to the four-layer model developed by the Department of Defense with the DoD Internet Layer omitted.
If the serial transport is used, the packet assembly is completed and placed on the transport media for delivery. If the packet will be sent over a LAN/WAN, the three DNP3 layers are rolled up into the application layer. The assembled packet is wrapped in the Transport Control Protocol (TCP) by the transport layer, which in turn is wrapped in the Internet Protocol (IP) by the internet layer. The User Datagram Protocol (UDP) can also be used but presents some additional issues related to reliable delivery in congested networks.
The fourth layer is the Network Interface layer where the assembled packet is actually interfaced to some type of transport media, such as twisted-pair copper, RG58 co-axial or fiber. While this multi-layer model may seem a bit confusing, it effectively isolates the tasks of communication and ultimately assists in designing and implementing a network.

## Slide 12: Module 03 – ICS Protocols
Modbus vs DNP3
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Feature | Modbus | DNP3
Transport | Serial / TCP/IP | Serial / TCP/IP
Model | Master-Slave | Master-Outstation (RTU-like)
Security (native) | None | Optional (DNP3 Secure Auth)
Time-stamps | Not Supported | Supported
Unsolicited Messaging | No | Yes
Complexity | Low | Medium-High
Bandwidth Efficiency | Moderate | High (with event buffering)
Notes: Instructor Notes:
This slide contrasts Modbus and DNP3 feature-by-feature. Modbus is simple but limited. DNP3 is more complex but offers superior features for modern, distributed monitoring systems. A key distinction is DNP3's ability to buffer and report events, which reduces bandwidth requirements and improves SCADA responsiveness.

## Slide 13: Module 03 – ICS Protocols
Wireshark Filters:
Modbus/TCP: tcp.port == 502
DNP3 (Ethernet/IP): tcp.port == 20000
DNP3 (Serial/Raw/IP): dnp3
Filter by Function Code:
  modbus.func_code == 3 (Read Holding Registers)
  dnp3.application.function == 1 (Read)
  Suricata Rule Example:
  alert tcp any any -> any 502 (msg:"Modbus Function Code 0x05 - Write Single Coil"; content:"|05|"; offset:7; depth:1; sid:1000001;)
Detecting Modbus and DNP3 Traffic
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
Wireshark is an invaluable tool for analyzing ICS protocol traffic. Using port-based and protocol-specific filters, instructors can walk students through inspecting Modbus TCP or DNP3 packet contents, function codes, and response behavior.
Suricata and Snort allow real-time detection via custom rules. The rules shown detect Modbus function code 0x05 (Write Single Coil) and DNP3 read requests (Function 0x01). These rules can be extended to monitor malicious behavior such as unauthorized write operations or unexpected broadcasts. Emphasize that ICS protocol monitoring should account for both protocol logic (e.g., read vs. write) and operational context (e.g., writing to critical coils outside scheduled maintenance windows).

## Slide 14: Module 03 – ICS Protocols
Schneider Electric / Modicon:
Modbus RTU, Modbus ASCII, Modbus TCP, Modbus Plus
Siemens:
Profibus, Profinet
Rockwell Automation / Allen-Bradley:
EtherNet/IP, ControlNet, DeviceNet
Emerson / FieldComm Group:
HART, FOUNDATION Fieldbus
Omron:
FINS
Panasonic:
MEWTOCOL
General (Open Standards):
OPC (DA, HDA, UA), DNP3, BACnet, MMS, IEC 60870, IEC 61850, and Modbus.
ICS Protocols by Vendor / Origin
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
Industrial vendors often develop proprietary or semi-proprietary protocols that dominate specific ICS ecosystems. For example, Modbus, originally developed by Modicon, is now an open protocol and extremely widespread due to its simplicity. Siemens leads with Profibus and Profinet, especially in Europe. Rockwell Automation systems often rely on EtherNet/IP, DeviceNet, and ControlNet, reflecting their dominance in North American manufacturing sectors.
Protocols like OPC UA, DNP3, and IEC 61850 are vendor-neutral and serve broader interoperability and utility grid applications. These categorizations help students understand where each protocol fits in real-world deployments and how to align tooling and detection strategies accordingly.

## Slide 15: Module 03 – ICS Protocols
Electric Power / Utilities:
IEC 60870-5-101/104, IEC 61850, DNP3, MMS
Water & Wastewater:
DNP3, Modbus RTU/TCP, OPC UA
Oil & Gas:
Modbus (RTU/TCP), OPC DA/UA, HART, FOUNDATION Fieldbus
Manufacturing / Discrete Automation:
EtherNet/IP, Profinet, DeviceNet, ControlNet
Building Automation:
BACnet, Modbus TCP, OPC UA
Pharmaceutical / Chemical:
Profibus PA, FOUNDATION Fieldbus H1, OPC UA
ICS Protocols by Use case and Industry
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
Different industrial sectors adopt communication protocols based on operational needs, existing infrastructure, and vendor relationships. Electric utilities require time-sensitive and standardized communication—hence the dominance of DNP3, IEC 61850, and MMS. Oil and gas pipelines often use Modbus and HART for legacy sensor systems.
Discrete manufacturing heavily uses Ethernet-based protocols like EtherNet/IP and Profinet due to their high speed and determinism. Building automation relies on BACnet for interoperability across HVAC, lighting, and security systems.
These distinctions help students recognize how protocols reflect industrial constraints, regulatory compliance, and integration strategies.

## Slide 16: Module 03 – ICS Protocols
CAN Bus (Controller Area Network)
Popular in automotive and industrial machinery.
Reliable, real-time control network for embedded devices.
DeviceNet
Built on CAN bus.
Common in Rockwell Automation systems.
ControlNet
Scheduled and unscheduled messaging.
Used for high-speed, deterministic control applications.
FINS (Factory Interface Network Service)
Proprietary protocol by Omron for communication between their PLCs and HMIs.
MEWTOCOL
Proprietary protocol by Panasonic for PLC communication.
TTCN (Tree and Tabular Combined Notation)
Used in protocol testing and validation in telecommunications and some ICS designs.
Other ICS Protocols
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
CAN BUS:
Overview:
Developed by Bosch in the 1980s, CAN Bus is a multi-master, message-based protocol.
Originally used in automotive networks, it’s now also common in industrial machinery and embedded control systems.
Key Features:
Deterministic: High priority messages are guaranteed timely delivery through arbitration.
Robustness: Excellent error handling and fault confinement.
No host-to-host addressing: Devices send messages to the network, and nodes decide if they should respond.
Bus topology: Often uses a two-wire differential pair (CAN_H and CAN_L).
ICS Use Cases:
Engineered systems such as robotic arms, industrial motor controllers, and embedded subsystems in manufacturing equipment.
ICS Security Implication:
Lacks encryption and authentication.
Susceptible to message injection and DoS without external protections.
DeviceNet
Overview:
Developed by Allen-Bradley (Rockwell Automation), DeviceNet is built on top of CAN Bus, adding an application layer for industrial automation.
Key Features:
Provides device-level communications between sensors, actuators, and controllers.
Uses object-oriented messaging to describe device behavior and data.
Supports plug-and-play capability via standardized profiles.
ICS Use Cases:
Integration of I/O modules, photoelectric sensors, and valves into PLC networks.
Common in Rockwell/Allen-Bradley industrial systems.
ICS Security Implication:
Inherits CAN Bus vulnerabilities.
Exposed DeviceNet networks are vulnerable to spoofing or control manipulation unless isolated.
ControlNet
Overview:
Also developed by Rockwell Automation, ControlNet is a deterministic, real-time control protocol for high-speed communications in automation systems.
Key Features:
Combines scheduled and unscheduled traffic:
  Scheduled traffic guarantees deterministic delivery (used for control loops).
  Unscheduled traffic is used for non-critical data (e.g., HMI updates).
Operates over coaxial or fiber-optic media.
ICS Use Cases:
High-speed control networks between PLCs and I/O chassis.
Often used in tandem with DeviceNet and EtherNet/IP in Rockwell architectures.
ICS Security Implication:
Not IP-based, which reduces external attack vectors.
However, insider threats or compromised serial gateways can still be problematic.
FINS (Factory Interface Network Service)
Overview:
FINS is a proprietary protocol by Omron, designed to unify communication across their range of industrial controllers and programming software.
Key Features:
Allows communication between:
  PLCs
  HMIs
  SCADA systems
  Engineering tools like Omron CX-Programmer
Supports multiple media: Ethernet, serial (RS-232/RS-485), and Controller Link.
ICS Use Cases:
Used in manufacturing plants that rely on Omron PLCs and machine automation systems.
Facilitates control, monitoring, and diagnostics across devices.
ICS Security Implication:
Proprietary, with little built-in security.
Typically relies on network segmentation and physical isolation for protection.
MEWTOCOL (Panasonic Protocol)
Overview:
MEWTOCOL stands for Matsushita Electric Works Protocol Communication Language.
A proprietary communication protocol developed by Panasonic (formerly Matsushita).
Key Features:
Serial-based ASCII protocol.
Provides command-response communication for reading/writing data, controlling timers, and more.
Often used with Panasonic FP series PLCs.
ICS Use Cases:
Machine tool control, packaging, and other discrete automation systems using Panasonic PLCs.
ICS Security Implication:
Clear-text protocol.
No encryption, authentication, or standard port-based controls.
Must be isolated from public or business networks.
TTCN (Tree and Tabular Combined Notation)
Overview:
TTCN is not a communication protocol, but a test specification language.
Originally developed for telecommunications protocol testing, it’s now applied in ICS protocol validation, especially during development or compliance testing.
Key Features:
Tabular and tree-based notation: Makes complex protocol behavior easier to test systematically.
Used to define test cases, test behavior, and data message formats.
Supports automated conformance and interoperability testing.
ICS Use Cases:
Protocol testing for standards like DNP3, IEC 61850, and proprietary ICS protocols.
Validation of new protocol implementations in control systems before deployment.
ICS Security Implication:
Not a live communication risk itself but is critical in verifying protocol robustness before ICS components are deployed in production.

## Slide 17: Module 03 – ICS Protocols
Level 0–1 (Field Level):
HART, Profibus PA, FOUNDATION Fieldbus H1
CAN Bus, DeviceNet, Modbus RTU/ASCII
Level 2 (Control Level):
Modbus TCP, EtherNet/IP, Profinet, ControlNet
OPC DA, MEWTOCOL, FINS
Level 3 (Operations Level):
OPC UA, IEC 60870-5-104, BACnet, IEC 61850
MMS, DNP3 over TCP/IP
Level 3.5 (DMZ/Gateway):
Firewalls, OPC UA Gateways, Protocol Converters
Level 4 (Enterprise Level):
Integration with MES/ERP using OPC UA or RESTful APIs
Not typically using real-time ICS protocols
ICS Protocols by Purdue Model Layer
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
The Purdue Enterprise Reference Architecture divides ICS networks into layered zones to separate operational technology (OT) from IT systems. At Levels 0–1, protocols focus on sensor and actuator communication, often over serial or bus-based media. HART, CAN Bus, and FOUNDATION Fieldbus are prominent here.
At Level 2, programmable logic controllers (PLCs) and distributed controllers use protocols like Modbus TCP, EtherNet/IP, and Profinet, which allow faster Ethernet-based control. Level 3 includes HMIs and SCADA servers that interface with data historians or visualization systems, often using OPC UA, DNP3, or IEC protocols for supervisory control and monitoring. Level 3.5 functions as a protective DMZ, housing protocol translators and firewalls, while Level 4 represents business networks that rarely engage directly with industrial protocols.

## Slide 18: Module 03 – ICS Protocols
Building Automation Systems (BAS) control HVAC, lighting, fire, and security systems.
Enhance energy efficiency, occupant comfort, and operational control.
BACnet (Building Automation and Control Network):
Open communication protocol for BAS (ASHRAE standard 135)
Supports multiple transport layers (Ethernet, IP, RS-485)
Object-oriented and vendor-neutral
Enables interoperability among devices from different manufacturers
BACnet/IP widely used in smart buildings and commercial campuses
Building Automation Systems (BAS) and BACnet
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
Building Automation Systems (BAS) are integral to modern commercial infrastructure, enabling centralized or distributed control over building functions like heating, ventilation, air conditioning (HVAC), lighting, access control, fire detection, and energy management.
The key protocol in this space is BACnet, developed by ASHRAE and adopted globally as a standard for open, interoperable building control. Unlike many industrial protocols that are proprietary or domain-specific, BACnet is object-based and vendor-neutral, allowing devices from different manufacturers to communicate seamlessly.
BACnet supports a variety of physical and data link layers, including:
BACnet/IP – over Ethernet for modern networks
BACnet MS/TP – over RS-485 for legacy and cost-sensitive systems
BACnet Ethernet – legacy support
Its data model consists of standardized objects (e.g., Analog Input, Binary Output, Schedule), each with defined properties, making device discovery, monitoring, and control straightforward.
Security considerations: Traditional BACnet lacked authentication and encryption, but modern deployments are adopting BACnet/SC (Secure Connect), which adds TLS-based security to protect communications.
BACnet is most commonly found in universities, hospitals, office buildings, and airports, and it plays a key role in the development of smart buildings and integrated facility management.

## Slide 19: Module 03 – ICS Protocols
Many ICS protocols lack encryption or authentication (e.g., Modbus RTU/TCP, DNP3)
Legacy serial protocols are vulnerable to physical tapping or man-in-the-middle attacks
OPC UA introduces better security (encryption, certificates) than OPC DA
Use of protocol converters may introduce attack surfaces (e.g., Modbus-to-TCP gateways)
Time-critical systems may resist updates that introduce latency (e.g., deep packet inspection)
ICS Security Considerations
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
Notes: Instructor Notes:
Security was often an afterthought in legacy ICS protocols, which were designed for isolated environments with little to no external connectivity. For instance, Modbus and DNP3 do not include built-in encryption or authentication, making them vulnerable to spoofing or replay attacks unless protected by external means like VPNs or firewalls.
Protocols like OPC UA have introduced security controls such as X.509 certificates, access control, and encryption, making them more suited for modern ICS networks. However, retrofitting security can be challenging due to legacy hardware and the need to avoid latency in control operations. Protocol gateways, while useful for integration, can be exploited if not hardened properly. This slide helps instructors bridge the gap between protocol functionality and cybersecurity posture.

## Slide 20: Module 03 – ICS Protocols
Lab 3 – PCAP Analysis (provided by instructor) of Modbus protocol & Grassmarlin (Labtainer) https://nps.edu/web/c3o/labtainer-lab-summary1#Industrial%20Control%20Systems
Course Title
CRN
©2021 CyberSkills2Work - Institution Name
CISA ICS CERT (210W-02 & 210W-03) https://www.cisa.gov/resources-tools/programs/ics-training-available-through-cisa
Notes: Instructor:
Guide the students on how to setup Wireshark to inspect the PCAP, which contains Modbus TCP traffic.
Remind students of the Modbus primer provided in the Softplc Labtainer instructions.